Robust Charging Infrastructure Design under Demand Uncertainty

A solar-powered charging station for a shared e-micromobility fleet — Executive Summary

Competition Themes — 3 (primary): solar-PV charging-station design  ·  2 (secondary): charge/discharge profiles under demand scenarios

| 25 kWp PV · 50 kWh · 4 chargers Recommended robust design | -60% (£31,574/yr) Value of robustness (worst-case cost) | 99% (vs 87% naive) Guaranteed fleet service, worst case | 84% (6.2 tCO2/yr) Operational carbon saving |
| --- | --- | --- | --- |

1. Problem Understanding    [20% criterion]

Shared e-micromobility fleets face highly variable charging demand — driven by season, weather, local events and multi-year growth. This creates a sizing dilemma for a solar charging station: a station built for average demand fails at peaks and strands the fleet, while one built for the worst case sinks capital into rarely-used equipment. The dilemma sharpens under a constrained grid connection — upgrading the connection needs a costly network reinforcement — so the evening charging peak must be served from on-site solar and storage. Sizing therefore becomes a decision under deep uncertainty: under-build and lose service; over-build and waste money. The demand range is grounded in the real national e-scooter trial monitoring dataset (monthly trips, fleet size, daily utilisation, trip distance), so the problem is posed on observed data rather than assumption.

2. Relevance & Innovativeness of the Proposed Solution    [20% criterion]

The solution directly delivers Theme 3 (design of a solar-PV charging station for a shared fleet) and Theme 2 (modelling charge/discharge profiles under demand scenarios), producing an actionable station specification with uncertainty bounds. Its novelty is methodological: charging-station sizing is almost always deterministic (a single demand forecast). We instead apply robust optimisation — minimax-regret and maximin — alongside a chance-constrained stochastic program, choosing a design that performs across the entire demand space, and we define and quantify the “value of robustness”: the worst-case cost and lost service avoided by hedging. A correlated Monte-Carlo “demand regime” reproduces the realistic co-movement of trips, utilisation and growth, and exposes a subtle but important result — expected-value design under-weights the correlated high-demand tail, which is precisely why scenario-based robust methods are required here.

3. Approach — Methodology, Algorithm & Flow    [20% criterion]

The pipeline (Figure 1) is: (i) build Low/Medium/High demand scenarios from the real trial data, scaled across a year-on-year growth range into nine probability-weighted scenarios; (ii) simulate an 8,760-hour energy balance for any design under the capped grid, dispatching PV → battery (with off-peak grid pre-charging for peak-shaving) → capped grid → unmet demand; (iii) evaluate all 150 designs (PV 5–25 kWp × battery 0–50 kWh × 4–20 chargers) against the nine scenarios, pricing unmet demand as lost service, to form a cost matrix; (iv) apply four decision rules — naive deterministic, chance-constrained stochastic, minimax-regret and maximin — and map the cost-vs-robustness Pareto frontier; (v) propagate uncertainty through a 500-sample correlated Monte-Carlo fan; (vi) rank the drivers with a tornado sensitivity analysis. The hourly controller is a transparent greedy priority rule (optimal for a single store) and the full study runs in about 25 seconds.

Figure 1 — End-to-end methodology / algorithm flow.

4. Feasibility of the Proposed Approach    [20% criterion]

Technical: the design uses only commercially available components — monocrystalline PV, a Li-ion battery (0–50 kWh) and standard AC charge points — sized within ranges supported by manufacturer datasheets and industry benchmarks. Economic: the recommended robust station has a ≈£68,400 capital cost and a bounded annual cost even in the worst demand scenario; the model reports CAPEX, OPEX, battery-replacement and grid costs. Operational: it yields one deployable specification plus the confidence interval around it. Computational: the entire model is open-source Python, deterministic, regenerates all data and figures from a single command, and is covered by an automated regression-test suite — so any reviewer can reproduce and audit every number.

5. Originality & Authenticity (AI / Plagiarism)    [20% criterion]

All model code, the dispatch engine, the optimisation formulation and every figure were written from scratch for this submission. The only redistributed dataset is the national DfT e-scooter monitoring data, reused under the Open Government Licence; the solar and grid-carbon series are physically modelled and calibrated to published references (with an optional live-API path), not copied. Every numerical assumption carries an inline source citation and all literature is referenced. The repository is fully self-contained and reproducible — fixed random seed, one-command rebuild, passing tests — directly supporting the competition’s AI and plagiarism checks. No third-party text or code is reproduced.

Figure 2 — Cost-vs-robustness Pareto frontier (four decision rules).      Figure 3 — Expected vs worst-case annual cost by rule.